## Slide 1: Building Heat Load Analysis
UPV-EHU, Bilbao, 2022-01-10/13

## Slide 2: Introduction
Learning outcomes
Index
Tools & data

## Slide 3: Learning outcomes
Energy & Cost
Understand the dynamics of energy loads in buildings
Understand hoy energy loads are converted into cost
Review variability sources in the energy loads & tariffs
Measurement & Verification
Understand the Measurement & Verification Concept
Review meter technology and data capture processes
Deliver assessment models
Modern Data Platforms & Analysis Techniques
Understand the potentialities of modern data platform to deliver more detailed models
Review data analysis methods

## Slide 4: Index
Day 1, Heat Loads in buildings
Heat loads in buildings
Heating & Cooling Cycles
DHW Cycles
Day 2, Measurement & verification
Measurement & Verification
Meters
EXERCISE
Day 3, Variability of Loads & Energy Carriers
Price of energy carriers
Variability
Data Quality
Day 4, Energy Management Platforms & Advanced Analysis Methods
Energy management platforms
Analysis methods
Revision of analysis methods
Wrap-up & Bonus materials

## Slide 5: Tools & Data
Data for one building in Tartu
  Heating load, hourly
  Climate, hourly
  Calendar & Bank Holidays
MS-EXCEL
  Enough for this seminar. But not for daily life.
  Students are strongly advised to pick & master one programming tool. Python, R,…

## Slide 6: Tools & Data
Data of one building in Tartu
  Heating load, hourly
  Climate, hourly
  Calendar & Bank Holidays
Calendar
Climate
ºC W/m2
Load
KW
or
KWh
Hourly data
Should be 8760h
But there is some data loss

## Slide 7: Heat loads in buildings
Energy balance Heating & Cooling
Relation to climate

## Slide 8: Energy balance Heating & Cooling
LESOSAI 5. Mode de Emploi. 2002.
https://docplayer.fr/57528916-Lesosai-5-calcul-du-bilan-thermique-d-une-construction-sia-380-1-en832-et-minergie.html
HEAT GAIN
People, appliances
Sun
Heating Systems
HEAT LOSS
Roof
Basement
Walls
Windows
Ventilation
Heat utilization factor
Heat losses,…
Domestic Hot Water
Domestic Hot Water

## Slide 9: Relation to climate
Heating & Cooling loads are correlated with outdoor temperatura
Cold Weather | High Heating Loads & Low Cooling loads
Hot Weather | Low Heating Loads & High Cooling loads
Large Solar Irradiation | Low(er) Heating Loads & High(er) Cooling loads
Greater Wind Speed | Variable impact ~High(er) Heating Loads & ~Low(er) Cooling loads

## Slide 10
Kottek, M., J. Grieser, C. Beck, B. Rudolf, and F. Rubel, 2006: World Map of the Köppen-Geiger climate classification updated. Meteorol. Z., 15, 259-263.
DOI: 10.1127/0941-2948/2006/0130.

## Slide 11: Relation to climate
Degree-Day Methods compute negative/positive deviations of daily mean ambient temperatures vs a reference temperature
Reference temperatures (typical)
  Heating Degree Days: 15ºC
  Cooling Degree Days: 23ºC
Reference temperatures are building dependent
  NZEB. HDD temp. ~10-12ºC
  Glazed building. HDD temp. ~20ºC

## Slide 12: Relation to climate
Daily Mean Temperature [ºC]
Reference Temperature, Heating [ºC]
Reference Temperature, Cooling [ºC]
Too cold to be confortable without heating
Too hot to be confortable without cooling

## Slide 13: Relation to climate
C
Daily Mean Temperature [ºC]

## Slide 14: Relation to climate
Chart: 

## Slide 15: Relation to climate
Chart: 
| 43800 | 43801 | 43802 | 43803 | 43804 | 43805 | 43806 | 43807 | 43808 | 43809 | 43810 | 43811 | 43812 | 43813 | 43814 | 43815 | 43816 | 43817 | 43818 | 43819 | 43820 | 43821 | 43822 | 43823 | 43824 | 43825 | 43826 | 43827 | 43828 | 43829 | 43830 | 43831 | 43832 | 43833 | 43834 | 43835 | 43836 | 43837 | 43838 | 43839 | 43840 | 43841 | 43842 | 43843 | 43844 | 43845 | 43846 | 43847 | 43848 | 43849 | 43850 | 43851 | 43852
HDD 12 | 2.7 | 2.9 | 5 | 5.1 | 2.4 | 3.8 | 2.8 | 1.1 | 0.9 | 2 | 0.8 | 1.3 | 0 | 0.2 | 0 | 0 | 2.4 | 1.5 | 0 | 1.1 | 1.3 | 0 | 0.6 | 0.3 | 1.1 | 1.2 | 5.4 | 5.3 | 5.4 | 5.8 | 5.5 | 5 | 5.7 | 5 | 3 | 3.9 | 6 | 4 | 3.4 | 0.8 | 2.1 | 4.2 | 6.6 | 3.6 | 0 | 0.4 | 0 | 1.6 | 2.5 | 3.1 | 6.2 | 7.7 | 4.9
HDD 14 | 4.2 | 4.9 | 7 | 7.1 | 4.2 | 5.4 | 4.3 | 2.6 | 2.5 | 3.5 | 2.6 | 2.8 | 0 | 0.6 | 0 | 0 | 4.4 | 2.3 | 0 | 2.8 | 2.5 | 1.3 | 1.6 | 1.2 | 2 | 1.7 | 7.1 | 6.9 | 7 | 7.4 | 7.3 | 6.7 | 7.4 | 7 | 5 | 5.8 | 7.9 | 5.6 | 4.9 | 2.2 | 4.1 | 6 | 8.3 | 5.1 | 0.7 | 0.9 | 0.1 | 3.3 | 4 | 5.1 | 8.2 | 9.7 | 6.9
HDD 15 | 5.1 | 5.9 | 8 | 8.1 | 5.2 | 6.4 | 5.1 | 3.6 | 3.5 | 4.3 | 3.6 | 3.7 | 0 | 1 | 0 | 0.5 | 5.4 | 2.8 | 0 | 3.6 | 3.2 | 2.2 | 2.3 | 1.8 | 2.4 | 2.3 | 8 | 7.8 | 7.9 | 8.3 | 8.3 | 7.7 | 8.3 | 8 | 6 | 6.8 | 8.9 | 6.5 | 5.7 | 2.9 | 5.1 | 7 | 9.3 | 6 | 1.3 | 1.2 | 0.2 | 4.1 | 4.8 | 6.1 | 9.2 | 10.7 | 7.9
HDD 16 | 6.1 | 6.9 | 9 | 9.1 | 6.2 | 7.3 | 6 | 4.6 | 4.5 | 5.1 | 4.6 | 4.7 | 0.2 | 1.4 | 0.1 | 1.3 | 6.4 | 3.4 | 0.2 | 4.6 | 4 | 3.2 | 3 | 2.5 | 2.9 | 3.2 | 9 | 8.7 | 8.8 | 9.3 | 9.3 | 8.7 | 9.3 | 9 | 7 | 7.8 | 9.9 | 7.3 | 6.6 | 3.8 | 6.1 | 8 | 10.3 | 7 | 1.9 | 1.6 | 0.5 | 5 | 5.6 | 7.1 | 10.2 | 11.7 | 8.9
HDD 18 | 8.1 | 8.9 | 11 | 11.1 | 8.2 | 9.3 | 7.9 | 6.6 | 6.5 | 7.1 | 6.6 | 6.7 | 1.9 | 2.8 | 1.2 | 3.3 | 8.4 | 4.8 | 1.2 | 6.5 | 5.7 | 5.2 | 5 | 4 | 4 | 4.9 | 11 | 10.7 | 10.7 | 11.3 | 11.3 | 10.7 | 11.3 | 11 | 9 | 9.8 | 11.9 | 9.2 | 8.4 | 5.5 | 8.1 | 10 | 12.3 | 9 | 3.9 | 3.4 | 1.4 | 7 | 7.6 | 9.1 | 12.2 | 13.7 | 10.9

## Slide 16
IDAE. Guía técnica Condiciones climáticas exteriores de proyecto. 2010
https://www.idae.es/uploads/documentos/documentos_12_Guia_tecnica_condiciones_climaticas_exteriores_de_proyecto_e4e5b769.pdf
HDD (15ºC)
HDD (20ºC)
CDD (20ºC)

## Slide 17
https://www.degreedays.net/

## Slide 18: Heat loads in buildings (summary)
Energy balance Heating & Cooling
  Buildings need to balance heat gain and loss to ensure a comfortable environment
  Heat is injected by means of heating appliances (e.g. boilers)
  Heat is removed by means of cooling appliances (e.g. air conditioning)
Relation to climate
  Various climates across the globe
  Temperature is the main index to define climate severity
  Loads can be indexed to mean outdoor temperature
  Heating/Cooling Degree Days are a common climate severity indicator
  Heating & Cooling loads are time/season dependent

## Slide 19: Heating & Cooling Cycles
Day-night
  Thermostat cycles
  Occupation
Week
Season
  De-activation in summer
  Criteria for re-activation
  Holidays

## Slide 20: Day-Night Cycles
Buildings are used unsteadily
  Residential buildings. Mainly at night
  Office & service buildings. ~8-17h
  Some exceptions: Hospitals, Data centres, Airports,…
    But even in these cases, there are specific patterns (sect. 7)
Heating is activated to meet occupant confort
  According to the aforementioned cycles
  Some technical adaptations
    Initiated before the actual occupation to ensure confort levels
    Deactivated slightly earlier than end of occupation to sabe Energy
    Background temperature levels are defined to avoid extreme low conditions.

## Slide 21: Weekly Cycles
Buildings are used unsteadily
  Residential buildings. Change patterns on weekends & holidays
  Office & service buildings. Commonly closed on weekends & holidays
  Some exceptions: Hospitals, Data centres, Airports,…
    But even in these cases, there are specific patterns (sect. 7)
Heating is activated to meet occupant confort
  According to the aforementioned cycles
  Some technical adaptations
    Shutdown
    Adaptation of actuation periods
      Manual/Automatic thermostats & operation of valves
    Background temperature levels are defined to avoid extreme low conditions

## Slide 22: Seasonal Cycles
Heating loads are higher in Winter & intermediate periods
There is a certain point in Spring where heating is no longer needed
DE-ACTIVATION METHODs
  Calendar. Performed manually by service crews
    e.g. 31st April (Spain).
  Climate. Implemented in control system
    e.g. 15 consecutive days with HDD=0
    e.g. 15 consecutive days with daily mean T>15ºC
    …
    (also performed manually by service crews*)
  Continously ON for specific buildings (Hospitals, Techical systems,…)

## Slide 23: Seasonal Cycles
There is a certain point in Autumn where heating is required again
ACTIVATION METHODs
  Calendar. Performed manually by service crews
    e.g. 15th October (Spain).
  Climate. Implemented in control system
    e.g. 7 consecutive days with HDD>0
    e.g. 7 consecutive days with daily mean T<12ºC
    …
    (also performed manually by service crews*)
    (when user calls the service manager*)

## Slide 24: Example
Sicheng Zhan, Zhaoru Liu, Adrian Chong, Da Yan, Building categorization revisited: A clustering-based approach to using smart meter data for building energy benchmarking, Applied Energy, Volume 269, 2020, https://doi.org/10.1016/j.apenergy.2020.114920
Freely available at https://ideaslab.io/publication/zhan-2020-building/
WARNING﻿: Magnitudes are normalized to daily maximum values.
  Daily MAX = 1

## Slide 25: Example
Daily (electricity) profiles
Sicheng Zhan, Zhaoru Liu, Adrian Chong, Da Yan, Building categorization revisited: A clustering-based approach to using smart meter data for building energy benchmarking, Applied Energy, Volume 269, 2020, https://doi.org/10.1016/j.apenergy.2020.114920
FIGURE 5

## Slide 26: Example
Daily (electricity) profiles
Sicheng Zhan, Zhaoru Liu, Adrian Chong, Da Yan, Building categorization revisited: A clustering-based approach to using smart meter data for building energy benchmarking, Applied Energy, Volume 269, 2020, https://doi.org/10.1016/j.apenergy.2020.114920
FIGURE 4

## Slide 27: Example
Daily (electricity) profiles
Different occupation period lengths:
Short working day
Longer working day
Extended afternoon periods
Sicheng Zhan, Zhaoru Liu, Adrian Chong, Da Yan, Building categorization revisited: A clustering-based approach to using smart meter data for building energy benchmarking, Applied Energy, Volume 269, 2020, https://doi.org/10.1016/j.apenergy.2020.114920
FIGURE 4

## Slide 28: Example
Daily (electricity) profiles
Different occupation period lengths:
Low afternoon activity
High afternoon activity
Sicheng Zhan, Zhaoru Liu, Adrian Chong, Da Yan, Building categorization revisited: A clustering-based approach to using smart meter data for building energy benchmarking, Applied Energy, Volume 269, 2020, https://doi.org/10.1016/j.apenergy.2020.114920
FIGURE 4

## Slide 29: Example
Calendar
Weekends
Vacation periods
Bank holidays
Sicheng Zhan, Zhaoru Liu, Adrian Chong, Da Yan, Building categorization revisited: A clustering-based approach to using smart meter data for building energy benchmarking, Applied Energy, Volume 269, 2020, https://doi.org/10.1016/j.apenergy.2020.114920
FIGURE 8

## Slide 30: Example
Share of profiles
(mostly) Residential
(mostly) Office
Morning
Morning+Afternoon
No predominance
Sicheng Zhan, Zhaoru Liu, Adrian Chong, Da Yan, Building categorization revisited: A clustering-based approach to using smart meter data for building energy benchmarking, Applied Energy, Volume 269, 2020, https://doi.org/10.1016/j.apenergy.2020.114920
FIGURE 13

## Slide 31: Heating & Cooling Cycles (Summary)
There are typical cycles in a building
  Day-night
  Weekday-wekend
  Season
  Bank Holidays
Each building has unique occupation profiles based on their type of use, HVAC systems, operation criteria,…

## Slide 32: DHW Cycles
Domestic Hot Water Preparation
Basic Engineering Formulation
Daily profile
Changes in cold water temperature. Impact on load
Holidays

## Slide 33: Domestic Hot Water preparation
~ Stable heat load (+-20%)
Calculations defined in building codes
  Water Flow
  Supply temperature
Source temperature defined by climate.
  Stable ~8-18ºC
Variations occur during the day

## Slide 34
Dwellings
Hospital
Health centre
l/day-person
CTE Documento Básico HE 4. Contribución solar mínima de agua caliente sanitaria
https://www.codigotecnico.org/images/stories/pdf/ahorroEnergia/DBHE.pdf
Rooms
People
Minimum ocupancy in residential buildings for DHW calculation

## Slide 35: Basic Engineering Formulation
Q = m * Cp * (T_sup – T_netw)
  m as defined in CTE HE4
  Cp = 4,18 kJ / (l*K)
  T_sup = 60 ºC
  T_source as per local climate
Bilbao: 9-17ºC

## Slide 36
E. Fuentes, L. Arce, J. Salom, A review of domestic hot water consumption profiles for application in systems and buildings energy performance analysis,
Renewable and Sustainable Energy Reviews, Volume 81, Part 1, 2018, Pages 1530-1547, ISSN 1364-0321, https://doi.org/10.1016/j.rser.2017.05.229.

## Slide 37: Daily Profile
E. Fuentes, L. Arce, J. Salom, A review of domestic hot water consumption profiles for application in systems and buildings energy performance analysis,
Renewable and Sustainable Energy Reviews, Volume 81, Part 1, 2018, Pages 1530-1547, ISSN 1364-0321, https://doi.org/10.1016/j.rser.2017.05.229.
E. Fuentes, L. Arce, J. Salom, A review of domestic hot water consumption profiles for application in systems and buildings energy performance analysis,
Renewable and Sustainable Energy Reviews, Volume 81, Part 1, 2018, Pages 1530-1547, ISSN 1364-0321, https://doi.org/10.1016/j.rser.2017.05.229.
FIGURE 4

## Slide 38: Daily Profile
E. Fuentes, L. Arce, J. Salom, A review of domestic hot water consumption profiles for application in systems and buildings energy performance analysis,
Renewable and Sustainable Energy Reviews, Volume 81, Part 1, 2018, Pages 1530-1547, ISSN 1364-0321, https://doi.org/10.1016/j.rser.2017.05.229.
E. Fuentes, L. Arce, J. Salom, A review of domestic hot water consumption profiles for application in systems and buildings energy performance analysis,
Renewable and Sustainable Energy Reviews, Volume 81, Part 1, 2018, Pages 1530-1547, ISSN 1364-0321, https://doi.org/10.1016/j.rser.2017.05.229.
FIGURE 5

## Slide 39: Holidays (months)
E. Fuentes, L. Arce, J. Salom, A review of domestic hot water consumption profiles for application in systems and buildings energy performance analysis,
Renewable and Sustainable Energy Reviews, Volume 81, Part 1, 2018, Pages 1530-1547, ISSN 1364-0321, https://doi.org/10.1016/j.rser.2017.05.229.
E. Fuentes, L. Arce, J. Salom, A review of domestic hot water consumption profiles for application in systems and buildings energy performance analysis,
Renewable and Sustainable Energy Reviews, Volume 81, Part 1, 2018, Pages 1530-1547, ISSN 1364-0321, https://doi.org/10.1016/j.rser.2017.05.229.
FIGURE 6

## Slide 40: Holidays (weekdays)
E. Fuentes, L. Arce, J. Salom, A review of domestic hot water consumption profiles for application in systems and buildings energy performance analysis,
Renewable and Sustainable Energy Reviews, Volume 81, Part 1, 2018, Pages 1530-1547, ISSN 1364-0321, https://doi.org/10.1016/j.rser.2017.05.229.
E. Fuentes, L. Arce, J. Salom, A review of domestic hot water consumption profiles for application in systems and buildings energy performance analysis,
Renewable and Sustainable Energy Reviews, Volume 81, Part 1, 2018, Pages 1530-1547, ISSN 1364-0321, https://doi.org/10.1016/j.rser.2017.05.229.
FIGURE 8

## Slide 41: Changes in cold water temperature. Impact on load
Flow Temperature: ~50ºC
Network Temperature: 9-17ºC
(assumption: constant consumption levels)
Max AT: ºC
Min AT: ºC
Bilbao: 9-17ºC
Variation: %
41
33
19,5
(41-33)/41 [%]

## Slide 42: DHW Cycles (Summary)
~ (seasonally) Stable heat load (+-20%)
Heavy intra-daily variations
Loads vary depending on type of building
  Dwellings: ~2 peak periods @early monring & late afternoon
  Restaurants: ~peak periods @ lunch & dinner time
  …

## Slide 43: Measurement & Verification
What is M&V
Why is it important
Key references
Estimating energy savings
Key concepts
Scopes/Approaches

## Slide 44: What is M&V
Define the performance of a system
  Absolute terms (e.g. one building/plant/…)
  Relative to a pre-existing baseline (e.g. building retrofit)
By means of measurement
Allowing for corrections
  Climate +-10-15% per year
  Variations in use calendar, work shifts, COVID-19
  Variations in system configuration retrofits, malfunctions,…
  Variations in cost of Energy +-5-30% depending on world-level market changes

## Slide 45: Why is it important (I)
Cycle of an Energy System
  Audit Oportunity is identified
  Basic Engineering Investment & Performance are Estimated
  Detailed Engineering Investment & Performance are Determined
  Construction Cost is executed
  Commissioning Performance is set
  Operation Energy is delivered
  Maintenance System performance is kept ~constant
Typically, different stakeholders are responsable of these ítems
  Owner
  Tenant
  Engineering offices
  Installer
  - Financing body
  - Maintenance company
  (with associated cost)

## Slide 46: Why is it important (II)
Cost and Performance Should be Accountable
Energy performance Contracts
  Increasingly common
    Get external financing
    Guarantee performance of the actual system
  Define payments based on actual performance
Performance
  Guarantee ≠Design
    ≠Rated
    ≠Estimated
    ≠Max
    ≠Min
  Definitions
    Energy [MWh], [%],…
    Currency [€/MWh], [max€],…

## Slide 47: Key references
ASHRAE 14, “Measurement of Energy, Demand and Water Savings”
CIBSE TM22: 2006, “Energy assessment and reporting method”
Efficiency Valuation Organization (EVO), International Performance Measurement and Verification Protocol (IPMVP)
ISO 50001:2018, Energy management systems — Requirements with guidance for use
  ISO 50002, Energy audits — Requirements with guidance for use
  ISO 50006, Energy management systems — Measuring energy performance using energy baselines (EnB) and energy performance indicators (EnPI) — General principles and guidance
  ISO 50047, Energy savings — Determination of energy savings in organizations
  Etc.
US DOE, “M&V Guidelines: Measurement and Verification for Federal Energy Projects”

## Slide 48: Estimating energy savings
Energy saving are avoided energy flows
  They are not actual energy flows.
  CAN NOT BE MEASURED
Savings are calculated as the difference two magnitudes
  Energy consumed if no intervention was done (Baseline)
  Actual consumption
These two items are measured in different time frames
  Corrections are required for climate & other factors

## Slide 49
Pre-intervention data
Used to construct a model
Post-intervention data
ACTUAL ENERGY USE
BASELINE
Model is fed with post-intervention data

## Slide 50
Mikel Lumbreras, Roberto Garay, Antonio Garrido Marijuan, Energy meters in District-Heating Substations for Heat Consumption Characterization and Prediction Using Machine-Learning Techniques,http://doi.org/10.1088/1755-1315/588/3/032007

## Slide 51: Key concepts
(Excerpt from ISO 50001)
Significant energy use, SEU: [Process/Areas within a Buliding/Factory with…] substantial energy consumption and/or offering considerable potential for energy performance improvement
  Boiler plant, chillers, thermal storage tanks, heat distribution y diffusion in buildings
  Industrial processes
  Transportation, fleets,… in some service companies
    Police, waste management companies,…
  Small office in Big Factory

## Slide 52: Key concepts
(Excerpt from ISO 50001)
Measurement: process to determine a value
  Meters & Counters
  Signal/Data validation criteria & procedures
  Agreed methods to determine performance/savings
Energy performance: Measurable result(s) related to:
  Energy efficiency (η, COP, W/lumen…)
  Energy use (kWh/m2.y, kWh/unit,…)
  Energy consumption (kWh,…)
Energy performance indicator
  Energy efficiency: … relationship between an output of performance, … and an input of energy (e.g. kWh/m2.y, kWh/unit)

## Slide 53: Key concepts
(Excerpt from ISO 50001)
Energy baseline: Reference(s) providing a basis for comparison of energy performance
  based on data from a specified period of time and/or conditions
  Typically equations referring the performance (e.g. kWh) against relevant variables (e.g. HDD), calibrated against a period (e.g. September 2017-August 2019)
Static factor: Factor that significantly impacts energy performance and does not routinely change
  e.g rented space in an office building
  If (relevant) changes are identified, the models/equations are adjusted. Likeliness ~10-20% per year
Relevant variable: Factor that significantly impacts energy performance and routinely changes
  E.g. weather, occupied rooms in a hotel, water consumption in a water treatment plant, amount of goods produced in a factory,…
  Models/equations already comprise these variables, so that their output is adapted in every analysis cycle
Risk/ uncertainty

## Slide 54: Scopes/Approaches
(IPMVP)
Typically 4 types of measurement/analysis scopes
  Option A: Partially Measured ECM Isolation
  Option B: ECM Isolation
  Option C: Whole Building Comparison
  Option D: Whole Building Calibrated Simulation

## Slide 55: Scopes/Approaches
(IPMVP)
Option A: Partially Measured ECM Isolation
  Analysis over only one subsystem
  Simplified measurements
Option B: ECM Isolation
  Analysis over only one subsystem
  Complete measurements
Typical applications
  Lighting
  HVAC, change of 1 system
  …

## Slide 56: Scopes/Approaches
Replacement of one boiler in a larger building

## Slide 57: Scopes/Approaches
(IPMVP)
Option C: Whole Building Comparison
  Analysis over full building/systems
  Full set of measurements
Typical applications
  Several interlinked interventions
  Renovation of windows, insulation of walls
  Changes to control system
  Changes to several HVAC appliances
  …

## Slide 58: Scopes/Approaches
Replacement of one boiler in a larger building
Variable Speed Drives
Changes to the building
Change to control criteria of heat production

## Slide 59: Scopes/Approaches
(IPMVP)
Option D: Whole Building Calibrated Simulation
  System does not exist before construction
  Simulation model. Calibrated against measurement data

## Slide 60: Scopes/Approaches
No pre-existing status.
Can not be measured
Build a model
Calibrate aganist
Post-construction data
Perform changes to the model
& assess baseline (blue line)

## Slide 61: Measurement & Verification (Summary)
Measurement of the performance of a system
  Improvements vs a baseline
  Allowing for corrections due to climate & use factors
Uses
  Performance-based contracts
  Corporate Energy Management Policies
Methods
  Some base methodologies
  Various scopes
  Adapted on a case-by-case basis (agreement between stakeholders)

## Slide 62: Meters
Electricity
Natural Gas
Heat
Fuels

## Slide 63: Electricity Meters
Smart meters deployed in EU.
Instantaneous metering available
In practical applications:
  Network stability ~1minute
  Large consummers ~10-15minute
  Regular applications ~1h

## Slide 64
Hourly consumption of a private household.
Ibformation available from Distribution Company.

## Slide 65
https://www.flickr.com/photos/traftery/4493063693
https://creativecommons.org/licenses/by-nc-sa/2.0/

## Slide 66: Natural Gas Meters
Smart meters not yet deployed.
(Very) large industries: Daily values
Others: monthly aggregated data
Device measures the delivered volumen: Nm3
Density & specific heat is tabulated per city, day & pressure level

## Slide 67: Natural Gas Meters
https://www.enagas.es/enagas/es/Gestion_Tecnica_Sistema/CalidadGas/CalidadGasMunicipio
Chart: 
~+- 1%
kWh/m3

## Slide 68: Natural Gas Meters
https://commons.wikimedia.org/wiki/File:Gas_meter.jpg Creative Commons Attribution-Share Alike 2.0 Austria

## Slide 69: Heat Meters
Devices that measure the heat delivered by an hydraulic heating/cooling system
A heat meter attached to a heat exchanger in a District heating substation in a residential neighborhood. Right in white-blue: the calculator; in the center in bronze: the ultrasonic flow meter, © Ulrichulrich CC BY-SA 3.0. link
https://www.kamstrup.com/en-en/heat-solutions/heat-meters/multical-303

## Slide 70: Heat Meters
https://youtu.be/LR0rQ5vK8do

## Slide 71: Heat Meters
https://youtu.be/LR0rQ5vK8do

## Slide 72: Heat Meters
Relevant Issue:
  Rounding errors. Particularly with low water Flow
  Meter stores integrated Energy:
    Supply: ∫ (volumen * T_supp)
    Return: ∫ (volumen * T_return)
  Delivered energy is calculated as a substraction from these two variables
Needs to be corrected for fluids other than water: Cp & density
Measurement error << 5% (EN-1434–1:2015)

## Slide 73: Other Fuels
No continous metering
  Unless especifically installed on-site.
Purchase invoices & delivery notes.
  i.e. 2017kg of biomass delivered on 2021/09/12
Uncertainties:
  Heat capacity
  Unaccounted storage of materials
    i.e. 375kg were already there before the unloading,…
    …423kg were not spent before the next unloading
  …
Mainly for liquid & solid fuels

## Slide 74: Meters (summary)
Electricity. Frequent data is available.
Natural Gas. Typically, bulk readings. i.e. monthly
Heat. Great progress towards frequent data.
Fuels. Bulk readings with large uncertainty

## Slide 75: Exercise
Heat load analysis of one building
Questions:
  Intial plot. Is there any visible trend or data group?
  Can this be explained by daily patterns?
  Can it be further explained by hourly patterns?
  Does the sun have any influence?
  Which is the relation of load to climate?

## Slide 76: Exercise
Heat load analysis of one building
Questions:
  Intial plot. Is there any visible trend or data group?

## Slide 78: Exercise
Heat load analysis of one building
Questions:
  Intial plot. Is there any visible trend or data group?
  YES. Two main slopes + horizontal section
  Can this be explained by daily patterns?

## Slide 80
Saturday & Sunday
Monday - Friday

## Slide 81: Exercise
Heat load analysis of one building
Questions:
  Intial plot. Is there any visible trend or data group?
  YES. Two main slopes + horizontal section
  Can this be explained by daily patterns?
  PARTIALLY. Weekends
  Can it be further explained by hourly patterns?

## Slide 82
0h to 5h
6h to 11h
12h to 17h
18h to 23h

## Slide 83
18h to 6h
9h to 16h
Transition:
7h
8h
17h

## Slide 84: Exercise
Heat load analysis of one building
Questions:
  Intial plot. Is there any visible trend or data group?
  YES. Two main slopes + horizontal section
  Can this be explained by daily patterns?
  PARTIALLY. Weekends
  Can it be further explained by hourly patterns?
  YES. Office pattern
  Does the sun have any influence?

## Slide 85
(Irradiation levels)

## Slide 86: Exercise
Heat load analysis of one building
Questions:
  Intial plot. Is there any visible trend or data group?
  YES. Two main slopes + horizontal section
  Can this be explained by daily patterns?
  PARTIALLY. Weekends
  Can it be further explained by hourly patterns?
  YES. Office pattern
  Does the sun have any influence?
  NOT REALLY
  Which is the relation of load to climate?

## Slide 87
Highly filtered data:
Mon-Thu
10-17h
Ambient temperatura <15ºC
Load > 25kWh
Use of linear regression procedure in EXCEL

## Slide 88
 | Value | Lower 95% | Upper 95%
Intercept | 123.66 | 122.40 | 124.92
Slope | -6.40 | -6.63 | -6.16

## Slide 89: Exercise
Heat load analysis of one building
Questions:
  …
  Which is the relation of load to climate?
  @0ºC ~123kW
  Rise per ºC ~6kW

## Slide 90: Acknowledgements
This project has received funding from the European Union’s Horizon 2020 research and innovation programme under grant agreement No 768567.
http://www.relatedproject.eu/
The data used in this exercise has been gathered within project RELaTED.

## Slide 91: Price of energy carriers
Tariff structure
Variations along the year.
  Electricity
  Natural gas
Demand-response & Interruptibility

## Slide 92: OUTDATED!!!
+100% +150%
X3 +100%
https://www.bloomberg.com/news/articles/2021-09-25/energy-crisis-puts-world-s-most-ambitious-climate-plan-to-test
(May be even worse when the lecture is delivered)

## Slide 93: Definition: Utility Company / Utility
https://www.collinsdictionary.com/us/dictionary/english/utility-company

## Slide 94: Tariff structure. Electricity
Focused at balancing the network
  Cost of infrastructure
  Cost of Energy production
Fixed + Variable cost structure
  Fixed. Connection fees
    Depends on installed/contracted power. (kW)
  Variable. Consumption
    Energy (kWh)
Consumption
Cost

## Slide 95: Tariff structure. Electricity
Connection fees
  Defined per contracted capacity (kW)
    Cosummer has the “right” to consume this capacity at any time
    If exceded, utilities can cut the delivery, or charge penalties
  Typically can be defined independently for specific periods
    e.g. Industry that operates at night can have a huge contracted capacity for those periods, and smaller capacity during peak hours.
    This leads to “explicit” capacity definition at energy network level

## Slide 96: Tariff structure. Electricity
Spain: IET 107/2014
…

## Slide 97: Tariff structure. Electricity

## Slide 98: Tariff structure. Electricity
Energy
  Defined by consumed Energy (kWh)
  Diferent Price for every hour
    Depends on wholesale cost of electricity
    Fixed based on production technologies for each hour and their costs at National/Regional level
€/MWh
time
Electricity, Energy, Spot value in Spain, 2020

## Slide 99: Tariff structure. Electricity
Chart: 
 | 41.88 | 38.6 | 36.55 | 32.32 | 30.85 | 30.14 | 30.17 | 30 | 30.65 | 30.65 | 30.27 | 30.34 | 30.99 | 30.04 | 30.75 | 32.11 | 35.98 | 40.4 | 44.05 | 46.16 | 44.02 | 45.6 | 42.9 | 37.55
Electricity, Energy, Spot price in Spain, 1st January 2020
+ 50 %
- 33%

## Slide 100: Tariff structure. Electricity
One Day Ahead prices for SWEDEN. (captured on 2021/03/17)
https://www.nordpoolgroup.com/Market-data1/Dayahead/Area-Prices/ALL1/Hourly/?view=chart

## Slide 101: Tariff structure. Natural Gas
Same Fixed + Variable cost structure as for Electricity
No intra-daily price variations
Cost comparison
(dwellings) | Fixed fee [€/month] | Variable fee [€/kWh]
Electricity | ~15€ | 0,06 - 0,13
Natural Gas | 8 | 0,04

## Slide 102
https://comparador.cnmc.gob.es/

## Slide 103: Variations
Year
Natural Gas
+300 %
- 60 %

## Slide 104: Variations
https://www.esios.ree.es/
Electricity spot Price. Daily averages
Spain
France
Other Western EU

## Slide 105: Demand-response & Interruptibility
Demand-response
  Avoid excessive costs: Prevent most expensive heat production systems
  Ensure that loads match the one-day ahead load forecast
  Distribute energy consumption throughout less-expensive periods of the day
    Economic suggestion + self- optimisation
Interruptibility
  Keep system stability: Electric suppliers need to keep the balance of the network: 50Hz (60Hz) at all times
  Compensate consumers to interrupt (fully or partially) energy supply
    Voluntary. Once signed for it, compulsory to interrupt upon short notice (i.e. 10 minutes)
(Electricity)

## Slide 106: Price of energy carriers (Summary)
Energy is a valuable resource
Complex & highly regulated environment
Energy is traded in international markets
There are relevant variations in the price of Energy carriers in the médium & long term
Electricity can not be stored in sufficient quantities
Electricity prices evolve on the short term (i.e. hours)

## Slide 107: Variability
Users
Non-explicit schedules
Confort
Failures
Pandemics

## Slide 108
Climate
???

## Slide 109: Users
Users behave slightly differently every day
Weather-normalized heat load patterns in a building. Lumbreras eta Al. (Unpublished)

## Slide 110: Users
“A London woman's love life and career both hinge, unknown to her, on whether or not she catches a train. We see it both ways, in parallel.”
https://www.imdb.com/title/tt0120148/
The Energy Load of a building varies depending on:
If you take the bus at 8:30 or you sleep 5’ more
If it’s raining and you leave jogging for tomorrow
You invite Friends to dinner
You are visiting a friend in Australia
You move to Belgium next semester
…

## Slide 111: Non-explicit schedules
Typical day
  Open to the public: 10-14h
  Employees
    Building open: 8-17h
    Working time: 8h. Some with reduced time (various reasons: Children, education,…)
    Interruptions: 2-3 (Coffee, lunch, short walk,…)
    Not same to all people
    Some work from home 2-3 days per week
Variations
  20-40% of personnel gets out of the office for some reason (meetings, seminars,…)
  2-5% of people are sick at home
Explicit

## Slide 112: Confort
Setpoints vary depending on user preferences
  Reference for heating: 20-22ºC (country dependent)
  Sleeping reference : ~19ºC
Buildings have some thermal inertia & need some time to adapt
  2-3 ºC of variation
  Temperature reduction: 2-5h with ~no load
  Temperature rise: 1-3h with increased load

## Slide 113: Confort
Users may prefer other temperature levels
24ºC
0ºC
10ºC
15ºC

## Slide 114: Failures & technical limitations
Systems do not always work as expected
District Heating systems
  Available energy may be limited by supply temperature & flow conditions
Electric systems
  Limitations to comply with contracted capacity
  Simultaneous use for heating & other applications
Liquid & Solid Fuels
  System may run out of fuel
All
  Limited to rated capacity of equipment (boiler, heat pump, substation,…)
  System stoped for repairs & maintenance

## Slide 115: Pandemics
Our weird behavior during the pandemic is messing with AI models
Machine-learning models trained on normal behavior are showing cracks —forcing humans to step in to set them straight.

## Slide 116: Variability (Summary)
Real life is more complex than rated setpoints & standard user profiles

## Slide 117: Data Quality
Voids/Gaps & how to fill them
Outliers

## Slide 118: Voids/Gaps & how to fill them
Modern data gathering systems
  Get frequent measurements
    Daily (non critical applications)
    Hourly (most heating & cooling systems)
    15-minutely (e.g. electricity sector)
    <1-minutely (control applications)
    …
  Transfer data to databases every short term
    ~Continous (control applications)
    <1-daily (any business-related system)
    >1-daily (applications to residential sectors)
    …

## Slide 119: Voids/Gaps & how to fill them
Systems fail (sometimes)
  Blackouts
    Batteries and UPS systems
  Failure in data/telephone connections
    GSM/3G/… connections are increasingly common for small applications
Systems are not perfect
  Internal memory gets full
  Systems reboot
  …
Systems are not sufficiently supervised
  Failures and errors are not detected & corrected promptly

## Slide 120: Voids/Gaps & how to fill them
So there is data loss
  Well designed/implemented/maintained systems <10%
  Others >10%

## Slide 121: Voids/Gaps & how to fill them
Example 1
  Data from heat meters.
  ~Good quality
(1 year = 8760h)
If a day starts at 0h, it should end at 23h
8760 – 8410 = 350 (~4-5%)

## Slide 122: Voids/Gaps & how to fill them
Example 2
  Data from cooling plant
  ~ bad quality
(some systems interpolate when there is missing data)

## Slide 123: Voids/Gaps & how to fill them
Example 2
  Data from cooling plant
  ~ bad quality
Normal Behavior
Normal Behavior (again)
Data loss
Last real data point
First real data point

## Slide 124: Voids/Gaps & how to fill them
Data from Tartu.
  January, 31 days. No data loss (in original dataset)

## Slide 125: Voids/Gaps & how to fill them
Are all days similar?

## Slide 126: Voids/Gaps & how to fill them
How many profiles?

## Slide 127: Voids/Gaps & how to fill them
How many profiles?

## Slide 128: Voids/Gaps & how to fill them
How to fill voids. OPTION 1. Linear interpolation

## Slide 129: Voids/Gaps & how to fill them
How to fill voids. OPTION 1. Linear interpolation

## Slide 130: Voids/Gaps & how to fill them
How to fill voids. OPTION 1. Linear interpolation

## Slide 131: Voids/Gaps & how to fill them
How to fill voids. OPTION 1. Linear interpolation
  OK for ~stable areas
  OK for ~homogeneous slopes
  TO BE IMPROVED for other areas

## Slide 132: Voids/Gaps & how to fill them
How to fill voids. OPTION 2. Replacement by typical day

## Slide 133: Voids/Gaps & how to fill them
How to fill voids. OPTION 3. Calculation of diferential profile
Chart: 
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
11 | 54.2 | 55.8 | 58.9 | 56.3 | 60 | 61.3 | 58.4 | 77.3 | 77.9 | 206.4 | 171.2 | 163.4 | 166.6 | 172.3 | 163.8 | 153.1 | 154.8 | 135.2 | 66 | 77.8 | 67 | 70.4 | 49.1 | 46.9
15 | 38.8 | 39.4 | 42.3 | 42.1 | 45.5 | 54 | 42 | 66.7 | 62.3 | 179.3 | 173.4 | 167.8 | 173 | 161.4 | 167.9 | 178.4 | 191.9 | 156 | 95 | 74.9 | 75 | 74.7 | 48.3 | 46.5
16 | 52.7 | 53.2 | 50.2 | 46.7 | 47.6 | 53.9 | 49.6 | 59.2 | 74.4 | 172 | 166.4 | 169.6 | 167.1 | 160.1 | 173.6 | 178.1 | 185.1 | 155.9 | 79.8 | 78.2 | 76.4 | 73.3 | 55.3 | 49.9
18 | 57 | 49.8 | 51.1 | 53.3 | 52.4 | 65.3 | 62.1 | 74.7 | 85.3 | 191.1 | 178.4 | 168.4 | 169.3 | 167.4 | 159.3 | 168.8 | 166.8 | 139.3 | 80.2 | 76.8 | 77.5 | 75.5 | 56 | 49.6
21 | 64.4 | 65.6 | 66.3 | 73.2 | 67.5 | 69.7 | 75.4 | 90.4 | 78 | 192.2 | 209.8 | 218.9 | 192.4 | 185.5 | 170.3 | 188.9 | 173 | 159.7 | 89.3 | 79.4 | 81.4 | 81.8 | 59.5 | 60.5
22 | 70.3 | 82.1 | 72.4 | 83.1 | 75.1 | 67.4 | 80.7 | 96.7 | 100.2 | 269.2 | 260.6 | 248.7 | 247.6 | 244.6 | 240.2 | 218.4 | 226.1 | 200.2 | 112.1 | 106.5 | 105.6 | 118.9 | 82.2 | 90.3
23 | 78.9 | 83.1 | 72.9 | 80.3 | 78.6 | 80.8 | 80.6 | 91.7 | 95.9 | 205.1 | 207.5 | 193.1 | 175 | 176.2 | 181.8 | 180.6 | 177 | 154.1 | 81.8 | 72.6 | 73.6 | 79 | 48.6 | 48.7
24 | 47.8 | 57.1 | 56.3 | 55.7 | 59.4 | 47 | 48.2 | 58.7 | 73.5 | 165.2 | 160.9 | 175.3 | 181.6 | 188.9 | 191.9 | 192.6 | 197.8 | 176 | 91.9 | 90 | 119.7 | 97.1 | 68.7 | 74.9
28 | 80.4 | 81.8 | 75.3 | 71.6 | 100.3 | 60 | 83.4 | 95.4 | 86 | 185.4 | 170 | 177.2 | 161.3 | 172.7 | 175.7 | 175.1 | 166.6 | 146.1 | 73 | 68.8 | 75.4 | 100.4 | 45.9 | 54.5
29 | 50.1 | 47.4 | 55.2 | 44.4 | 48.5 | 43.6 | 49.9 | 52.5 | 74.9 | 202.8 | 196.4 | 192.8 | 196.4 | 186.1 | 180 | 176 | 187.5 | 150.1 | 83.4 | 71.5 | 70.3 | 67.9 | 43.4 | 41.6
31 | 54.4 | 53.8 | 57.5 | 62.1 | 60.4 | 52.3 | 66.5 | 71.1 | 98.9 | 200.6 | 196.5 | 206.4 | 198.8 | 177 | 179.7 | 184.1 | 178 | 166.1 | 89.9 | 90.6 | 84.7 | 82.2 | 62 | 59.8
MEAN | 59 | 60.8273 | 59.8545 | 60.8 | 63.2091 | 59.5727 | 63.3455 | 75.8545 | 82.4818 | 197.2091 | 190.1 | 189.2364 | 184.4636 | 181.1091 | 180.3818 | 181.2818 | 182.2364 | 158.0636 | 85.6727 | 80.6455 | 82.4182 | 83.7455 | 56.2727 | 56.6545

## Slide 134: Voids/Gaps & how to fill them

## Slide 135: Voids/Gaps & how to fill them

## Slide 136: Voids/Gaps & how to fill them
Other Options
Johra, H., Leiria, D., Heiselberg, P., Marszal-Pomianowska, A., Tvedebrink, T., Treatment and analysis of smart energy meter data from a cluster of buildings connected to district heating: A Danish case
(2020) E3S Web of Conferences, 172, art. no. 12004, DOI: 10.1051/e3sconf/202017212004

## Slide 137: Outliers
There is typically a certain amount data which is not consistent
  Measurement errors
  Abnormal behavior
This data should be removed
Data removal should be consistent
  Remove one data point?
  Remove full day?
  Remove full week?
  Remove preceding and succeeding interval?

## Slide 138: Outliers
Guidance
  Remove a small ammount of data
    Typically ~<2,5-5%
  Remove data within its context
    If analysis is performed by month:
      Subset “January”, then identify outliers
      (extreme data means differnt things in January or in June)
  ASHRAE 14. Table 14-2
    Maximum 25% of data, should be properly explained
    SEEMS TO BE TOO LOOSE.

## Slide 139: Outliers
7,5 to 12,5 ºC

## Slide 140: Outliers
Very few points
(Data below 25kWh is discarded)

## Slide 141: Outliers
Discarding criteria:
Standard Deviation: Data which is farther tan 2*Sd from the mean
Inter-Quartile: Data which is farther tan IQR from the mean. IQR=Q3-Q1
Standard deviation IQR

## Slide 142: Outliers
Standard deviation IQR
Remove
Which criteria is best?

## Slide 143: Data Quality (Summary)
There is a lot of data in modern systems
Some times:
  Systems fail (hopefully <10%)
  Data is incorrect (outliers)
    Faulty data should be filtered-out
Datasets need to be repaired
Repair techniques need to be fit for purpose
  Interpolation
  Typical values
  Typical evolution

## Slide 144: Energy management platforms
Evolution
  Handling large datasets
  Modern user experience
Commercial tools
Applications
  Benchmarking
  M&V processes
  Alerts
Data pipeline. Hardware/Software/Cloud/User

## Slide 145: Evolution. Handling large datasets
https://www.flickr.com/photos/ejk/808461304 (CC BY-SA 2.0)

## Slide 146: Evolution. Handling large datasets
https://www.flickr.com/photos/151112035@N05/31610696003 (CC BY-NC-SA 2.0)

## Slide 147: Evolution. Handling large datasets
https://commons.wikimedia.org/wiki/File:U-SQL.gif (CC BY-SA 4.0)

## Slide 148: Evolution. Handling large datasets

## Slide 149: Evolution. Modern user experience
https://www.smarkia.com/es

## Slide 150: Commercial tools
(some)
  https://www.smarkia.com/
  https://www.dexma.com/
  https://www.ekiom.com/en/
  http://genio.pro/
  https://www.wattics.com/
  https://www.energis.cloud/en/
  https://linkener.com/
  https://seinon.org/
  …

## Slide 151: Commercial tools
In most cases, for specific uses
  Retail: multi-point, low complexity
  Malls: high complexity, HVAC focused
  PV plants
  EV charging spots: Multi-point, invoicing
  Industry: Highly customizable
  Condos: Multi-customer
Various purposes
  Supervision
  Alerts
  Benchmarking
  M&V
  Invoicing
  Remote management

## Slide 152: Commercial tools
According to public information, all vendors deliver same quality & functionality
  This is almost false
  There is a need to clearly define customer needs and map them to the management platforms to make a good choice
Connectivity to third party (on-site) hardware is easy
  This is quite true (& improving)

## Slide 153: Commercial tools

## Slide 154: Applications. Insights
https://www.smarkia.com/en

## Slide 155: Applications. Benchmarking
https://www.azavea.com/projects/energy-benchmarking/

## Slide 156: Applications. M&V processes
Samir Touzani, Jessica Granderson, David Jump, Derrick Rebello, 2019, Evaluation of methods to assess the uncertainty in estimated energy savings, Energy and Buildings 193, https://doi.org/10.1016/j.enbuild.2019.03.041

## Slide 157: Applications. Submetering & allocation

## Slide 158: Applications. Alerts

## Slide 159: Applications. Reports

## Slide 160: Data pipeline. Hardware/Software/Cloud/User
Item | Scale | Type | Operation | Data storage
Sensors & actuators | Field activity | Physical | Continous ~Real time | No
Local system | Building / Facility level | Physical | Continous ~ Near Real time | ~< 1week
Cloud | Multi-building / Facility | Virtual | Supervision* ~>1day | No limit

## Slide 161: Energy management platforms (Summary)
Gather information from many buildings
Simplify the user experience
  No need for IT & communication knowledge
  No need for investement in hardware & connectivity
  Data is properly managed & backed up
  Accessible through web-app
  No need for programming skills
  Perform most of the low-level activities
  Can focus on delivering relevant outcomes
Caution
  Verify thay you understand what the system is doing
  Verify that data can be accessed & exported
    Advanced applications
    Migration to new vendor

## Slide 162: Analysis methods
Energy Signature & Regression
Decision Trees Gradient Boosting & Random Forrest
Neural Networks
Clustering

## Slide 163: Energy Signature & Regression
PRISM
Ashrae Changepoint
Multivariable
Method Extension

## Slide 164: PRISM
1973 Oil Crisis
  Initial policies for Energy conservation
  First standardized methods ~1970/80
PRISM
  PRInceton Scorekeeping Method
https://www.businessinsider.com/gas-signs-1970s-2011-8#-18

## Slide 165: PRISM
Margaret F. Fels, PRISM: An introduction, Energy and Buildings, 1986, https://doi.org/10.1016/0378-7788(86)90003-4
Margaret F. Fels, PRISM: An introduction, Energy and Buildings, 1986, https://doi.org/10.1016/0378-7788(86)90003-4
FIGURE 1a & 4a

## Slide 166: PRISM
Margaret F. Fels, PRISM: An introduction, Energy and Buildings, 1986, https://doi.org/10.1016/0378-7788(86)90003-4
Margaret F. Fels, PRISM: An introduction, Energy and Buildings, 1986, https://doi.org/10.1016/0378-7788(86)90003-4
FIGURE 4b & TABLE 1

## Slide 167: PRISM
Margaret F. Fels, PRISM: An introduction, Energy and Buildings, 1986, https://doi.org/10.1016/0378-7788(86)90003-4
Margaret F. Fels, PRISM: An introduction, Energy and Buildings, 1986, https://doi.org/10.1016/0378-7788(86)90003-4
EQUATIONS 3 & 4

## Slide 168: PRISM
Margaret F. Fels, PRISM: An introduction, Energy and Buildings, 1986, https://doi.org/10.1016/0378-7788(86)90003-4
HDD reference temperature 20ºC
Baseload 1.12kWh/day
Thermal sensitivity 400Wh/day
Climate-related load
107 GJ/year
(over actual climate)
142,5 GJ/year
(over reference climate)
Margaret F. Fels, PRISM: An introduction, Energy and Buildings, 1986, https://doi.org/10.1016/0378-7788(86)90003-4
TABLE 1

## Slide 169: PRISM
Margaret F. Fels, PRISM: An introduction, Energy and Buildings, 1986, https://doi.org/10.1016/0378-7788(86)90003-4
Robust method
Based on few data
Filters-out transitory effects
Starting point for more modern methods

## Slide 170: Ashrae Changepoint
Margaret F. Fels, PRISM: An introduction, Energy and Buildings, 1986, https://doi.org/10.1016/0378-7788(86)90003-4
FIGURE 4a
Kissock, J.K., Jeff S Haberl, and David E. Claridge. 2002. “Development of a Toolkit for Calculating Linear, Change-Point Linear, and Multiple-Linear Inverse Building Energy Analysis Models.”
Changepoint
HDD
TEMPERATURE

## Slide 171: Ashrae Changepoint
Replaces the Degree-Day approach for a “changepoint” temperatura approach
Generalizes PRIMS for a variety of loadds
  Heating
  Cooling
  Heating & Cooling
  Multi-sloped loads

## Slide 172: Ashrae Changepoint
More parameters are calculated (p)
More observations are needed (i)
  i > 20 * p
The validation process is more complex
Applicability over data with greater resolution
  Phenomena not associated to outdoor ambient temperatura is visible
Mitchell T. Paulus, David E. Claridge, Charles Culp, Algorithm for automating the selection of a temperature dependent change point model, Energy and Buildings, https://doi.org/10.1016/j.enbuild.2014.11.033

## Slide 173: Multivariable
Additional variables can be considered
  Solar radiation
  Calendar
  Ocupancy level
    ~Electric load?
  Temperature/load in previous days
  …

## Slide 174: Multivariable
Additional variables can be considered
  Solar radiation

## Slide 175: Multivariable
Additional variables can be considered
  Solar radiation
  Calendar
Sicheng Zhan, Zhaoru Liu, Adrian Chong, Da Yan, Building categorization revisited: A clustering-based approach to using smart meter data for building energy benchmarking, Applied Energy, https://doi.org/10.1016/j.apenergy.2020.114920
Sicheng Zhan, Zhaoru Liu, Adrian Chong, Da Yan, Building categorization revisited: A clustering-based approach to using smart meter data for building energy benchmarking, Applied Energy, Volume 269, 2020, https://doi.org/10.1016/j.apenergy.2020.114920
FIGURE 8

## Slide 176: Multivariable
Additional variables can be considered
  Solar radiation
  Calendar
  Ocupancy level
    ~Electric load?
Xin Liang, Tianzhen Hong, Geoffrey Qiping Shen, Improving the accuracy of energy baseline models for commercial buildings with occupancy data, Applied Energy, https://doi.org/10.1016/j.apenergy.2016.06.141
Xin Liang, Tianzhen Hong, Geoffrey Qiping Shen, Improving the accuracy of energy baseline models for commercial buildings with occupancy data, Applied Energy, https://doi.org/10.1016/j.apenergy.2016.06.141
FIGURE 7

## Slide 177: Method Extension
Larger number of explainatory variables
Indicators of building usage
  Occupamcy of parking lot, canteen,…
  Eater consumption (cold and/or hot)
  Electric consumption (Computers/plug loads)
  Status of internet connection
  Meeting room booking system
  Calendar, vacations,…
  …

## Slide 178: Method Extension
Transitories & thermal inertia
  Climate
    Average climate data T-24h..T
    (Was yesterday colder than today?)
  Building usage (days after holidays?)
    Average heat load T-24h..T
    (Was the boiler active yesterday?)

## Slide 179: Method Extension
(Indirect)
Data segmentation for typical periods & calibration for each one
    Season Systems turned off in summer
    Weekday Weekly patterns & thermal inertia, holidays
    Hour Daily patterns, (i.e. lunch)
    Hour of the week
    (other specific patterns for specific buildings)

## Slide 180: Decision Trees, Gradient Boosting & Random Forrest
Decision Trees
Gradient Boosting
Random Forrest

## Slide 181: Decision Trees
Data is subsetted
Then a value/model is developed for each area
Three different representations of a classification tree of kyphosis data, Stephen Milborrow, https://en.wikipedia.org/wiki/Decision_tree_learning#/media/File:Cart_tree_kyphosis.png CC BY-SA 4.0

## Slide 182: Decision Tree
Mikel Lumbreras, Roberto Garay-Martinez, Beñat Arregi, Koldobika Martin-Escudero, Gonzalo Diarce, Margus Raud, Indrek Hagu, Data driven model for heat load prediction in buildings connected to District Heating by using smart heat meters, Energy, 2022, https://doi.org/10.1016/j.energy.2021.122318

## Slide 183: Decision Tree
Mikel Lumbreras, Roberto Garay-Martinez, Beñat Arregi, Koldobika Martin-Escudero, Gonzalo Diarce, Margus Raud, Indrek Hagu, Data driven model for heat load prediction in buildings connected to District Heating by using smart heat meters, Energy, 2022, https://doi.org/10.1016/j.energy.2021.122318

## Slide 184: Gradient Boosting
Real Relationship Y~f(X) (unknown)
All models are imperfect
                Y_e1~g(X) !=f(X)
There is an error (gradient)
grad_e1 = Y – g(X)

## Slide 185: Gradient Boosting
Differential model
grad_e1 ~ h(X) != Y – g(X)
Aggregation of both models
Y_e2 ~ g(X) + h(X) !=f(X)
Y – g(X)-h(X) < Y-g(X)
iterate…g(X), h(X), I(X), J(X),…

## Slide 186: Gradient Boosting (note)
Differential model
grad_e1 ~ h(X) != Y – g(X)
Functions do not need to be continous, derivable,…relaciones contínuas, derivables,…
  i.e.: h(X) = 35 (X>10)
  h(X) = 40 (X<=0)

## Slide 187: Gradient Boosting
https://en.wikipedia.org/wiki/Gradient_boosting

## Slide 188: Gradient Boosting
https://www.geeksforgeeks.org/ml-gradient-boosting/

## Slide 189: Random Forrest
Several inperfect models. Each of these:
  Calibrated aganist a different subset of observations
  Using only a subset of available explainatory variables
Result is averaged
Diagram of a random decision forest
Venkata Jagannath - https://community.tibco.com/wiki/random-forest-template-tibco-spotfirer-wiki-page
CC BY-SA 4.0

## Slide 190: Neural Networks
Several (simple) functions are chained to create a complexnetwork
An example artificial neural network with a hidden layer
https://en.wikipedia.org/wiki/Artificial_neural_network#/media/File:Artificial_neural_network.svg
CC BY-SA 3.0
Temperature
Solar Radiation
Month
Hour
…
Heat load
…

## Slide 191: Neural Networks
Typical functions
https://en.wikipedia.org/wiki/Activation_function

## Slide 192: Review of analysis methods
What is the purpose of the analysis?
  Short term load forecasting
  Unbiased projection of models in the long term
  Physical meaning
  Models for extrapolation to other operational conditions
NOTE: All this may not be achievable with the same model

## Slide 193: Review of analysis methods
Short term load forecasting
  Large input datasets.
    Many signals: Climate, use, internal conditions, heat load
    Historical values: ~6h-7x24=144h
  Complex models
    Neural networks??
  Potential risk for overfitting & validity limited to a short term

## Slide 194: Review of analysis methods
Unbiased projection of models in the long term
  Main relationship with climate
    Lenear / Squared models with 2-4 main variables
  Accurate models over aggregated periods (~daily, weekly,…) but highly unaccurate in specific observations (~hourly,…)
  Stable in the long term (~years?)
  Options
    Linear Regresion
    Support Vector Regression
    Gradient boosting
    Decission Trees (?)

## Slide 195: Review of analysis methods
Physical significance
Regresion
  Potentially with some segmentation

## Slide 196: Review of analysis methods
Extrapolation to other operational conditions
AVOID models with hidden criteria
  Decission Trees
  Neuronal Networks
Alternatives
  Linear Regresion
  Support Vector Regression
  Gradient boosting*

## Slide 197: Wrap-up & Bonus material
Energy assessment
  Increasingly complex with new data streams
  Increasingly powerful with new data streams
  Needs to be directed to particular applications
  Highly ingfluenced by meter resoluation & data quality
Energy Costs
  Very relevant to consummers
  Influenced by user profiles & cost profiles
  May need to be monitored under performance contract environments
Modern data platforms
  Facilitate the delivery of assessments
  There is still a need for relevant knowledge in the field of Energy modelling

## Slide 198: Bonus materials
Github repository: https://github.com/robgaray/SMACCS_Building_Heat_Load_Analysis.git
  These slides
  Data
  Assessment (Exercise on Day 2)
(some) relevant researchers in this field
  Granderson, Jessica, https://www.scopus.com/authid/detail.uri?authorId=14630354400
  Chong, Adrian, https://www.scopus.com/authid/detail.uri?authorId=57189900965
  Hong, Tianzhen, https://www.scopus.com/authid/detail.uri?authorId=7202830430
  Mor, Gerard, https://www.scopus.com/authid/detail.uri?authorId=56443716500
  Bacher, Peder, https://www.scopus.com/authid/detail.uri?authorId=27667564700

## Slide 199: Bonus materials
Self work
  (all works) https://orcid.org/0000-0003-2331-6561
  Data driven model for heat load prediction in buildings connected to District Heating by using smart heat meters, Energy, 2022, https://doi.org/10.1016/j.energy.2021.122318
  Unsupervised Clustering for Pattern Recognition of Heating Energy Demand in Buildings Connected to District-Heating Network, https://doi.org/10.5281/zenodo.5583260
  Energy meters in District-Heating Substations for Heat Consumption Characterization and Prediction Using Machine-Learning Techniques, https://doi.org/10.1088/1755-1315/588/3/032007
  Data driven process for the energy assessment of building envelope retrofits, https://doi.org/10.1051/e3sconf/202017225001
  Regression analysis of the energy consumption of tertiary buildings, https://doi.org/10.1016/j.egypro.2017.07.290

## Slide 200: Acknowledgements
This project has received funding from the European Union’s Horizon 2020 research and innovation programme under grant agreement No 768567.
http://www.relatedproject.eu/
A relevant share of the data presented in this lecture has been gathered within project RELaTED.